## Slide 1: PAIRS project update
Dec 17th, 2021
Amanda Farnsworth

## Slide 2: Outline
Wind turbine power model and results (slides 3-4)
Solar power model and results (slides 5-6)
TEA for solar and wind (slides 7-8)
City level comparison (slide 9)
Standard deviation and coefficient of variation (slides 10)
Next steps (slides 11)
Additional solar equations (slides 12)

## Slide 3: Model for turbine output
P = air * Cp * A * v3 / 2 [2]
P: power = variable in W
air: density of air = 1.23 kg/m3
Cp: maximum power coefficient = 0.4 (theoretical maximum = 0.59)
A: sweep area of blades = 11,309 m2 (60m radius with nameplate capacity of 2.55 MW [3])
v: wind speed = variable in m/s
[1 ]NY-Wind-Energy-Guide.pdf
[2] https://www.raeng.org.uk/publications/other/23-wind-turbine
[3] https://www.energy.gov/eere/articles/wind-turbines-bigger-better
[1]

## Slide 4: Tracking wind output over time
[4] https://websites.pmc.ucsc.edu/~jnoble/wind/extrap/
[5] https://www.windpowerengineering.com/calculate-wind-power-output/
CF = AEO / (366 * 24 * MRC) [5]
CF = capacity factor
AEO = annual energy output in Wh
MRC = manufacturers rated capacity
Check:
CF = 5 * 109 / (366 * 24 * 2.55 * 106)
CF = 22%
*note: some unusually low capacity factors present (lowest = 0.122%)
Extrapolating wind speed from 10m to 40m above the surface
v2 = v1 * (z2/z1)a [4]
z: height in m
v: windspeed in m/s
a: wind shear component = 0.2
subscripts 1 and 2 indicate height at 10m and 40m, respectively
*note: a varies hourly and regionally. Incorporate this into next version.

## Slide 5: Model for PV output
[6] Dobos, A. P. PVWatts Version 5 Manual. www.nrel.gov/publications. (2014)
[7] Gilman, P. et al. SAM Photovoltaic Model Technical Reference Update. www.nrel.gov/publications. (2016).
Assumptions
Equations used:
Sandia Temperature model – gives cell temperature (Tcell) (slide 12)
1)  = nom * (1 +  * (Tcell – Tref)) [6]
: efficiency
nom: rated efficiency
: constant -0.47 %/C
Tref: reference temperature = 25 C
2) PDC = I * A *  * flosses [7]
A: cell area in m2 (slide 6)
I: irradiance in W/m2
flosses: compilation of all listed losses = 0.895
PDC: hourly direct current power output
Cell type = Si
Installation type = utility, fixed tilt
ILR = 1
Rated efficiency = 26%
Shading losses = 3%
Soiling losses = 2%
Wiring losses = 2%
Connection losses = 0.5%
Degradation losses = 1.5%
Availability losses = 2%
3) PAC = PDC * inv [6]
inv: inverter efficiency
PAC: hourly alternating current power output

## Slide 6: Tracking solar output over time
[8] https://www.eia.gov/todayinenergy/detail.php?id=38272
[9] https://www.ilumen.be/en/the-difference-between-nominal-and-real-pv-power-explained/
[10] https://www.hisour.com/nominal-power-in-photovoltaic-39514/
[11] https://www.windpowerengineering.com/calculate-wind-power-output/
Assumed: Prating = 50MW [8]
A = Prating / (MRC * Istc) [9]
Istc: irradiance at standard conditions = 1,000 W/m2
A = 50,000,000 / (0.26 * 1,000)
A = 190,000 m2
Check: ~ 5 m2 / kW [10]
190,000 / 50,000 = 3.8 m2 / kW
CF = AEO / (366 * 24 * MRC) [11]
CF = capacity factor
AEO = annual energy output in Wh
MRC = manufacturers rated capacity
Check:
CF = 60 * 109 / (366 * 24 * 50 * 106)
CF = 14%

## Slide 7: Translation of PV power output to TEA
Assumptions
Lifetime = 30 years
Interest rate = 4%
Check with SESAME (in Boston):
51.7 $/MWh via PAIRS calculations vs. 50.7 $/MWh via SESAME web
2% difference caused by different weather data sources
[12] https://sesame.mit.edu/app/costs
[12]

## Slide 8: Translation of wind power output to TEA
Assumptions
Lifetime = 30 years
Interest rate = 2.5%
Tax rate = 25.74% (federal and state)
Check with NREL [13]:
37 $/MWh via NREL vs. large range via PAIRS calculations
36.5 $/MWh when LCOE calculations done with NREL assumed capacity factor (0.42)
 LCOE calculations are sound
 CF calculations are error source
Suspected source of error:
wind speed extrapolation inaccuracies – wind shear value should be ~0.4 for mountain ranges [14]
[13] https://sesame.mit.edu/app/costs
[14] https://www.researchgate.net/publication/329162512_A_Probabilistic_Assessment_Approach_for_Wind_Turbine-Site_Matching
Increasing wind shear exponent from 0.2 to 0.4

## Slide 9: City level comparison
Solar values are correct vs. wind values need slight correction
Excluding Denver wind results with a change in y-axis

## Slide 10: Standard deviation and coefficient of variation
Regions of high output have high variability
Regions of low output have the high coefficient of variation
Wind has a higher coefficient of variation than solar

## Slide 11: Next steps
Correct wind extrapolation calculations
Complete LCA for wind and solar
Repeat analysis on different years of data
**check in with another PowerPoint**
Aggregate data and repeat analysis at aggregated level
  Compare aggregated results to results at high resolution
Use high resolution data with only irradiance* data aggregated
  Compare results to results at high resolution
  Repeat with * = wind or temp

## Slide 12: Solar equations
[15] https://pvpmc.sandia.gov/modeling-steps/2-dc-module-iv/cell-temperature/pvsyst-cell-temperature-model/
[16] https://www.pvsyst.com/help/thermal_loss.htm
Sandia temp model: Tc = Ta + Epoa * * ( 1 – etam) / (U0 + U1 * v) [15]
Tc : cell temp = variable C
Ta : ambient temp = variable C
Epoa : irradiance incident = 0.1 W / m2
: absorption coefficient = 0.9
etam : efficiency of PV module = 0.1
U0 : constant heat transfer component = 25 W/ m2 * K & U1 : convective component = 1.2 W / m2 * K / (m/s) [16]